## Read me
Alarm rationalisation worksheet
From Enco Group (enco.au)
What this is | A worksheet that asks the rationalisation questions of every candidate alarm, in the order ISA-18.2 and IEC 62682 set them out: the cause, the consequence of no action, the operator's action, the time to respond, and from those the priority, the setpoint and the deadband. An alarm with no operator action is removed, with the reason recorded.
The rule | An alarm is an indication to the operator of a condition requiring a response. No response, no alarm. The lifecycle, the philosophy and the measures are explained at https://enco.au/articles/alarm-management
How to use it | Work system by system with an operator, a process or control engineer and a facilitator. Fill every column for every candidate before deciding Keep. Priority comes from the philosophy's matrix of consequence against time to respond, never from how worried anyone is. The five example rows are a crusher lubrication system; delete them before use. The Measures sheet holds the benchmarks to report against monthly.
Terms of use | Free to use and adapt. Provided as a starting point, without warranty, and not a substitute for a site's own alarm philosophy.
Column | What goes in it
Tag | The point in the control system
Description | What the alarm is, in words
Alarm type | As it says (drop-down: High, High high, Low, Low low, Deviation, Rate of change, Discrete, Fault)
Cause | What has happened in the process when this alarm comes in
Consequence of no action | What happens if the operator does nothing
Consequence class | From the philosophy's scale (drop-down: None, Minor, Major, Severe)
Operator action | The specific action the operator takes. If there is none, this is not an alarm
Time to respond | How long the operator has before the consequence, from the process dynamics (drop-down: Under 3 min, 3 to 10 min, 10 to 30 min, Over 30 min)
Priority | From consequence and time to respond, by the philosophy's matrix (drop-down: Low, Medium, High, Critical)
Setpoint | The value, with its basis
Deadband or delay | To stop chattering, from the signal's noise
Keep | As it says (drop-down: Yes, No)
Reason if removed | Duplicate, no action, covered by another alarm, diagnostic not alarm
Rationalised by, date | As it says

## Rationalisation
Tag | Description | Alarm type | Cause | Consequence of no action | Consequence class | Operator action | Time to respond | Priority | Setpoint | Deadband or delay | Keep | Reason if removed | Rationalised by, date
CR-001-PT-101 | Crusher lube oil pressure low | Low | Lube pump tripped, filter blocked, line leak or oil low | Bearing damage within minutes, crusher trip at low low | Major | Start the standby pump; if pressure does not recover in 1 minute, stop feed and shut down | Under 3 min | High | 180 kPa, from the bearing supplier's minimum plus margin | 10 kPa deadband | Yes |  | Rationalisation team, 2026-10-29
CR-001-PT-101 | Crusher lube oil pressure low low | Low low | As above, pressure continued to fall | Crusher trips on this value by interlock | Major | None beyond confirming the trip and following the restart procedure | Under 3 min | Low | 150 kPa |  | No | Trip event, not an alarm: logged as an event with the interlock | Rationalisation team, 2026-10-29
CR-001-TT-102 | Lube oil return temperature high | High | Cooler fouled, cooling water low, bearing running hot | Oil viscosity falls, bearing wear accelerates over hours | Minor | Check cooling water flow and cooler differential; raise a work order | Over 30 min | Low | 65 degrees, from the oil specification | 2 degree deadband | Yes |  | Rationalisation team, 2026-10-29
CR-001-LT-103 | Lube oil tank level low | Low | Leak or consumption | Pump cavitation and the pressure low alarm follows | Minor | Top up and inspect for leaks | 10 to 30 min | Low | 40 per cent | 5 per cent deadband | Yes |  | Rationalisation team, 2026-10-29
CR-001-FLT-104 | Lube oil filter differential high | High | Filter loading normally | None in the shift; the standby filter is selected by hand at the next round | None | None by the operator; the planner schedules the change | Over 30 min | Low |  |  | No | No operator action: a maintenance notification from the historian, not an alarm | Rationalisation team, 2026-10-29
Note on A1: The point in the control system
Note on B1: What the alarm is, in words
Note on D1: What has happened in the process when this alarm comes in
Note on E1: What happens if the operator does nothing
Note on F1: From the philosophy's scale
Note on G1: The specific action the operator takes. If there is none, this is not an alarm
Note on H1: How long the operator has before the consequence, from the process dynamics
Note on I1: From consequence and time to respond, by the philosophy's matrix
Note on J1: The value, with its basis
Note on K1: To stop chattering, from the signal's noise
Note on M1: Duplicate, no action, covered by another alarm, diagnostic not alarm

## Measures
Measure | Benchmark, per operator console | Why it matters
Average alarm rate | Fewer than 1 per 10 minutes, about 150 a day | About 2 per 10 minutes, 300 a day, is the most that is manageable
Peak alarm rate | Fewer than 10 in any 10 minutes | A flood is more than 10 in 10 minutes
Time in flood | Less than 1 per cent of hours | During a flood the operator cannot read the alarms, so each one is noise
Stale alarms | Fewer than 5 standing for more than 24 hours | A standing alarm nobody acts on trains the operator to ignore the screen
Chattering and fleeting | None | An alarm that cycles more than a few times a minute is a deadband or delay problem
Priority distribution | About 80 per cent low, 15 per cent medium, 5 per cent high | If most alarms are high priority, the priorities mean nothing
Top ten contributors | Less than 1 per cent of the load each | A handful of bad actors usually make most of the load
Suppressed out of service | All known and tracked | An alarm suppressed and forgotten is a protection that is gone

## Lifecycle
Stage | What it does | What it produces
Philosophy | Sets the site's rules once: what an alarm is for, the priorities and their meaning, the performance targets, the roles | The alarm philosophy document
Identification | Finds candidate alarms from the hazard studies, the control narrative, the operating procedures and incident history | A list of candidates, each with a reason
Rationalisation | Tests every candidate against the philosophy: consequence, operator action, time to respond, priority, setpoint | The master alarm database, with the ones that failed the test removed
Detailed design | Specifies how each alarm is implemented: deadband, delay, suppression, shelving, the display | Configuration ready to load
Implementation | Loads and tests the configuration, trains the operators on the new alarms and their responses | Alarms live, with the response written against each
Operation | Operators respond to alarms, shelve nuisances under rules, and report what the system does badly | Alarm and response history
Maintenance | Alarms out of service for maintenance are tracked and returned; faulty instruments fixed rather than suppressed | Out-of-service log
Monitoring and assessment | Measures the system against the targets: rates, floods, stale and chattering alarms, priority distribution, the bad actors | A monthly performance report
Management of change | Any new or changed alarm goes through rationalisation again, not straight into the control system | The master alarm database stays the truth
Audit | Periodic check that the lifecycle is being followed, and the philosophy still fits the plant | Audit findings into the philosophy