## Read me
FAT and SAT checklist template
From Enco Group (enco.au)
What this is | A test record for a factory acceptance test and a site acceptance test: one row per test, with what is tested, how, the expected result written before the test from the design documents, the actual result after, a pass or fail, the punch item raised for a fail, and who tested and witnessed it.
The rule | The expected result is written from the narrative, the cause and effect matrix or the specification before the test runs. A result filled in from what was observed cannot fail and proves nothing.
How to use it | Number the tests within the procedure, F- for the factory test and S- for the site test. Group them by category in the order on the Categories sheet, because each depends on the one before. Every fail gets a punch reference and a retest. Do not sign the record with open fails that have no punch item. The eight example rows are from a conveyor control system's FAT and SAT; delete them before use. The reasoning is at https://enco.au/articles/factory-and-site-acceptance-testing
Terms of use | Free to use and adapt. Provided as a starting point, without warranty, and not a substitute for a project's own test procedures or the vendor's.
Column | What goes in it
Test no. | Numbered within the procedure
System | The system or panel under test
Category | As it says (drop-down: Documents, Inspection, Power-up, IO check, Logic and interlocks, Sequences, Alarms and trips, HMI, Communications, Failure modes, Documentation)
Test | What is tested, in one line
Method | How: what is forced, operated or measured, and with what
Expected result | From the narrative, the cause and effect or the specification, never from what happened
Actual result | What was observed, in the same terms
Result | As it says (drop-down: Pass, Fail, N/A, Deferred)
Punch ref | The punch item raised for a fail
Tested by | As it says
Witnessed by | The owner's representative
Date | As it says
Comments | As it says

## Test record
Test no. | System | Category | Test | Method | Expected result | Actual result | Result | Punch ref | Tested by | Witnessed by | Date | Comments
F-01 | CV-201 MCC panel | Documents | Drawings and software at the test revision | Compare the drawing register against the drawings supplied; compare the PLC program version against the FDS revision | All drawings at rev C or later; PLC program 1.4 | Loop diagram LOOP-0117 supplied at rev B | Fail | P-0412 | Vendor test engineer | Owner's control engineer | 2026-09-14 | Rev C issued during the test; retested F-01 passed
F-12 | CV-201 MCC panel | IO check | ZS-201A belt drift switch input | Operate the simulator contact for DI 3.07; observe the PLC input and the HMI | DI 3.07 goes true; HMI shows ZS-201A Drift; alarm raised at priority 2 | As expected | Pass |  | Vendor test engineer | Owner's control engineer | 2026-09-15
F-31 | CV-201 MCC panel | Logic and interlocks | Belt drift trip on either switch | Force ZS-201A then ZS-201B true in turn with the conveyor running in simulation | Conveyor stops on either input within 1 s; restart inhibited until reset | Stopped on ZS-201A; no stop on ZS-201B | Fail | P-0419 | Vendor test engineer | Owner's control engineer | 2026-09-15 | Logic change under MOC-2026-044 not in program 1.4; fixed in 1.5 and retested
F-40 | CV-201 MCC panel | Sequences | Start sequence with downstream permissive | Simulate CR-001 feed permissive; initiate start from HMI | Pre-start siren 10 s, then drive start; no start without the permissive | As expected | Pass |  | Vendor test engineer | Owner's control engineer | 2026-09-16
S-05 | CV-201 field | IO check | ZS-201B belt drift switch loop check | Operate the switch at the tail by hand; observe the PLC input and the HMI | DI 3.08 goes true; HMI shows ZS-201B Drift | As expected | Pass |  | Site control technician | Owner's maintenance supervisor | 2026-10-21
S-18 | CV-201 field | Logic and interlocks | Belt drift trip from the field switch | With the conveyor running empty, operate ZS-201B by hand | Conveyor stops within 1 s; CR-001 feed inhibited; alarm and event logged with the right time | Stopped in 0.8 s; event time 3 min behind the historian | Fail | P-0501 | Site control technician | Owner's control engineer | 2026-10-22 | PLC clock not synchronised to the site time source; fixed and retested
S-27 | CV-201 field | Communications | Belt weigher WT-201 totaliser to the historian | Run the belt with the test chain; compare the weigher display, the HMI and the historian tag | All three agree within the weigher's stated accuracy | As expected | Pass |  | Site control technician | Owner's control engineer | 2026-10-22
S-33 | CV-201 field | Failure modes | Loss of the network link to the control room | Disconnect the fibre at the MCC switch for 30 s, then reconnect | Conveyor keeps running on local control; HMI shows comms loss; data backfilled on reconnect | Conveyor ran; HMI alarm raised; 30 s gap in the historian not backfilled | Fail | P-0507 | Site control technician | Owner's control engineer | 2026-10-23 | Store and forward not enabled on the gateway; raised with the vendor
A test marked Fail with no punch reference is a test that was stopped, not finished. Raise the item, retest when it is closed, and only then sign.
Note on A1: Numbered within the procedure
Note on B1: The system or panel under test
Note on D1: What is tested, in one line
Note on E1: How: what is forced, operated or measured, and with what
Note on F1: From the narrative, the cause and effect or the specification, never from what happened
Note on G1: What was observed, in the same terms
Note on I1: The punch item raised for a fail
Note on K1: The owner's representative

## Summary
Category | Pass | Fail | N/A | Deferred | Not run
Documents
Inspection
Power-up
IO check
Logic and interlocks
Sequences
Alarms and trips
HMI
Communications
Failure modes
Documentation
Total

## Categories
Category | What is checked | At the FAT | At the SAT
Documents | The drawings, the narrative, the cause and effect, the IO list and the software are at the revision the test is written against | Yes | Yes, updated from the FAT punch list
Inspection | Panels, labels, terminations, earthing, segregation, spare capacity, against the drawings and the specification | Yes | Installation and field wiring
Power-up | Supplies, voltages, redundancy, failover of power supplies and processors, battery and UPS behaviour | Yes | On site power, with the real UPS
IO check | Every input and output on the IO list, end to end, at the right address, the right range and the right engineering units | To a simulator or a test panel | To the field device: the loop check
Logic and interlocks | Every cause in the cause and effect produces every effect, and nothing else | Yes, by forcing | Yes, from the field device where it can be done safely
Sequences | Start, stop, hold and restart sequences run as the narrative says, including the abnormal paths | Yes | Yes, with the real drives and valves
Alarms and trips | Each alarm at its setpoint, priority and message; each trip to its final element | Yes | Yes, and the trip timed where it matters
HMI | Graphics match the P&ID, every tag is on a display, navigation and permissions work, trends and the historian record | Yes | With the site displays and accounts
Communications | Links to other systems: the DCS, the historian, the MES, the drives, the weighers, the third-party packages | Only what can be brought to the factory | Yes, the main thing the SAT adds
Failure modes | Loss of power, loss of a network link, a processor failover, a bad input, a restart from cold | Yes | Yes, with the real network
Documentation | The manuals, the backups, the as-tested configuration, the licence records and the punch list handed over | At the end of the test | At the end of the test

## Stages
Stage | Where | What it proves | What leaves it
Design review | Engineering office | The specification, the control narrative, the cause and effect and the IO list agree with each other and with the P&ID | Reviewed documents at an issued revision, the test procedure drafted from them
FAT | Vendor's works | The system as built and configured does what the specification says, tested against simulated inputs before it leaves the factory | The signed test record, the punch list, the configuration backup taken at the end of the test
Delivery and installation | Site | The system arrived as tested, was installed to the drawings and wired to the field | Inspection and test records, the installation punch list
SAT | Site, installed and connected | The system works with the real field devices, the real network, the real power and the other systems it talks to | The signed test record, the loop check sheets, the punch list, the as-left configuration backup
Commissioning | Site, with process material | The plant does what the design said under real conditions, system by system | Functional and performance test records, the pre-startup safety review