## Read me
Plant document register template
From Enco Group (enco.au)
What this is | The index of every controlled document on a plant: its number, revision, state, owner, where the master is held and where copies are posted, and the equipment tags it describes so it can be found from the asset.
The rules | A number is never reused and never changes; the revision is in its own column. The plant runs on the as-built revision. A superseded revision is withdrawn from every point of use. The reasoning, the states and the numbering elements are explained at https://enco.au/articles/document-control-plant
How to use it | One row per document. When a revision is issued, update the revision, state, date, change reference and supersedes columns on the same row, and withdraw the posted copies listed under points of use. The four example rows are one conveyor; delete them before use. The States and Numbering sheets are the conventions to adapt.
Terms of use | Free to use and adapt. Provided as a starting point, without warranty.
Column | What goes in it
Document number | Never reused and never changed. The revision is in its own column
Title | As it says
Type | As it says (drop-down: PID, GA, SLD, SCH, LOOP, CE, FD, DS, VDR, PROC, JP, REG)
Discipline | As it says (drop-down: Process, Mechanical, Electrical, Instrumentation, Control, Civil, Operations, Maintenance)
Area or system | From the plant breakdown
Equipment tags | The tags the document describes, so it can be found from the asset
Revision | As it says
State | As it says (drop-down: Draft, IFR, IFC, As-built, Superseded, Cancelled)
Issue date | As it says
Owner | The person or role accountable for its content
Held in | The system of record and its path or id
Points of use | Where copies are posted: control room, substation, the CMMS job plan
Change reference | The management of change or project that produced this revision
Supersedes | The revision this replaced

## Register
Document number | Title | Type | Discipline | Area or system | Equipment tags | Revision | State | Issue date | Owner | Held in | Points of use | Change reference | Supersedes
SITE-200-P-PID-0012 | Conveyor CV-201 and transfer station P&ID | PID | Process | 200 | CV-201, TS-201 | AB 2 | As-built | 2026-09-14 | Process lead | EDMS, folder 200/PID | Control room drawing set; CMMS job plans JP-ME-040 to 046 | MOC-2026-031 | AB 1
SITE-200-E-SLD-0003 | Substation 2 single line diagram, CV-201 drive | SLD | Electrical | 200 | CV-201-M1, SS2-CB-07 | AB 1 | As-built | 2026-03-02 | Electrical lead | EDMS, folder 200/SLD | Substation 2 wall set | PRJ-2025-08 | IFC 0
SITE-200-I-LOOP-0117 | Loop diagram, CV-201 belt drift switch ZS-201A | LOOP | Instrumentation | 200 | CV-201-ZS1 | IFC 0 | IFC | 2026-10-20 | I and C lead | EDMS, folder 200/LOOP |  | MOC-2026-044
SITE-200-S-CE-0002 | Cause and effect, conveyor CV-201 protection | CE | Control | 200 | CV-201 | AB 1 | As-built | 2026-03-02 | Control lead | EDMS, folder 200/CE | Control room; PLC program header | PRJ-2025-08 | IFC 0
Note on A1: Never reused and never changed. The revision is in its own column
Note on E1: From the plant breakdown
Note on F1: The tags the document describes, so it can be found from the asset
Note on J1: The person or role accountable for its content
Note on K1: The system of record and its path or id
Note on L1: Where copies are posted: control room, substation, the CMMS job plan
Note on M1: The management of change or project that produced this revision
Note on N1: The revision this replaced

## States
State | Revision code | What it means | May be used for
Draft | A, B, C | Being written or checked. Not issued | Nothing outside the authoring team
Issued for review | IFR | Circulated for comment by the disciplines and the owner | Comment. Not construction, not operation
Issued for construction | IFC, revision 0 | Approved. The document the plant is built or modified from | Construction, procurement, commissioning
As-built | AB, revision 1 onward | Marked up from the field at handover and reissued to show what was actually built | Operation, maintenance, the next modification
Superseded | S | Replaced by a later revision. Kept, never used | History only. Withdrawn from every point of use
Cancelled | X | The subject no longer exists. Kept with the decommissioning record | History only

## Numbering
Element | What it says | Example
Site or project | Which facility the document belongs to | PRJ, or the site code
Area or system | Where in the plant, from the same breakdown the hierarchy and the commissioning systems use | CR for crushing, 200 for the conveyor system
Discipline | Which discipline owns it | P process, M mechanical, E electrical, I instrumentation, C civil, S control
Document type | What kind of document, from a fixed list | PID, GA, SLD, LOOP, CE, DS, PROC
Sequence | A number that makes it unique within the above | 0012
Revision | Its state and issue, carried separately so the number never changes | C, IFC 0, AB 1, AB 2

## Document kinds
Document | What it holds | Owner | Changed by
P&IDs | Every line, valve, instrument and interlock on the process, by tag | Process engineering | Any modification to the process. The first drawing a change touches and the last to be updated
General arrangements and layouts | Where everything is, in plan and elevation | Mechanical and civil | Anything moved, added or removed
Single line diagrams and schematics | The electrical system from the supply to each load, and the control circuits | Electrical | Any electrical change, including a changed protection setting
Loop diagrams and I/O lists | Every instrument from the field to the controller, terminal by terminal | Instrumentation and control | Any instrument, cable or I/O change
Cause and effect, functional descriptions | What the control system does and why: interlocks, trips, sequences | Control engineering | Any logic change, which is most changes
Datasheets and vendor documents | What each item of equipment is, its ratings, its maker's manuals and drawings | The discipline that specified it | Replacement with anything not identical
Control system configuration | The PLC programs, HMI projects, settings and backups | Control engineering | Every logic or display change. Backed up on change, not on a schedule
Procedures and job plans | How the plant is operated and maintained, step by step | Operations and maintenance | Any change that alters a step, a limit or a hazard
Registers | The asset register, the hierarchy, the document register itself | Asset management | Every change to what exists or what describes it