## Read me
Preventive maintenance checklist template
From Enco Group (enco.au)
What this is | A checklist with a failure mode and a pass criterion against every preventive task, a task library by equipment class to start from, and a review sheet that asks whether each task is earning its place.
The loop it runs in | 1. Failure modes: The failure modes worth managing, by criticality 2. Tasks and intervals: A task per failure mode, with an interval and its basis 3. Program: Maintenance plans in the CMMS, grouped into routes and shutdown packages 4. Execute and record: Readings and findings on the work order, defects raised as work 5. Review: Intervals corrected, tasks removed or added, from findings and failures
How to use it | Checklist tab: one row per task per item. Fill the task, kind, failure mode, interval and pass criterion when the program is built, and the reading, pass, finding and work order when the task is done. Task library tab: example tasks by equipment class; copy the ones that fit and delete the rest. Review tab: the signals to look for, task by task, starting with the equipment that costs the most.
The rule | Every task names the failure mode it manages, every pass criterion is a reading or a limit, and every finding becomes a work order the same day. The reasoning is at https://enco.au/articles/preventive-maintenance-program
Terms of use | Free to use and adapt. Provided as a starting point, without warranty, and not a substitute for a site's own analysis.
Column | What goes in it
Tag | The functional location or equipment number the task belongs to
Equipment | As it says
Task | What is done, stated so a tradesperson new to the site could do it
Kind | The kind of preventive task (drop-down: Fixed interval, Inspection, Condition monitoring, Failure finding)
Failure mode managed | The failure this task exists to prevent or find. A task with nothing here is a candidate for removal
Interval | The number, with the unit beside it
Unit | As it says (drop-down: Hours, Weeks, Months, Tonnes, Cycles)
Running or stopped | Whether the task needs the equipment out of service (drop-down: Running, Stopped)
Pass criteria | A reading, a limit or a condition. Never a tick on its own
Reading or result | What was measured or seen. Filled in when the task is done
Pass | As it says (drop-down: Y, N)
Finding | What was found if it did not pass, in enough words to raise a work order
Work order raised | The corrective work order number for a finding
Done by | As it says
Date | As it says

## Checklist
Tag | Equipment | Task | Kind | Failure mode managed | Interval | Unit | Running or stopped | Pass criteria | Reading or result | Pass | Finding | Work order raised | Done by | Date
Note on A1: The functional location or equipment number the task belongs to
Note on C1: What is done, stated so a tradesperson new to the site could do it
Note on D1: The kind of preventive task
Note on E1: The failure this task exists to prevent or find. A task with nothing here is a candidate for removal
Note on F1: The number, with the unit beside it
Note on H1: Whether the task needs the equipment out of service
Note on I1: A reading, a limit or a condition. Never a tick on its own
Note on J1: What was measured or seen. Filled in when the task is done
Note on L1: What was found if it did not pass, in enough words to raise a work order
Note on M1: The corrective work order number for a finding

## Task library
Equipment class | Task | Kind | Failure mode managed | Interval | Unit | Running or stopped | Pass criteria
Centrifugal pump | Check seal for leakage and record drip rate | Inspection | Mechanical seal face wear | 1 | Weeks | Running | No visible leakage; drip rate within the seal vendor's limit
Centrifugal pump | Vibration readings at drive end and non-drive end bearings | Condition monitoring | Bearing wear, misalignment, imbalance | 4 | Weeks | Running | Overall velocity below the alarm limit for the pump class and no rising trend
Centrifugal pump | Replace bearings and seal, check shaft and wear rings | Fixed interval | Bearing fatigue, seal wear | 16000 | Hours | Stopped | Shaft runout and wear ring clearance within the pump manual limits
Electric motor | Winding insulation resistance test | Condition monitoring | Insulation breakdown | 12 | Months | Stopped | Insulation resistance above the minimum for the voltage class, corrected to 40 degrees
Electric motor | Grease bearings with the specified grease and quantity | Fixed interval | Bearing lubricant degradation | 2000 | Hours | Running | Quantity as per the motor nameplate or lubrication chart; old grease purged
Gearbox | Oil sample for analysis | Condition monitoring | Gear and bearing wear, oil degradation, contamination | 3 | Months | Running | Wear metals, viscosity and water within the limits for the oil and gearbox
Gearbox | Check breather, oil level and for leaks | Inspection | Oil loss, contamination through the breather | 1 | Weeks | Running | Level in the sight glass range; breather clean; no active leak
Conveyor | Route inspection: idlers, pulleys, skirts, cleaners, structure, guards | Inspection | Seized idlers, belt damage, carryback, structural wear | 1 | Weeks | Running | No seized or noisy idlers; cleaners in contact; no carryback build-up; guards secure
Conveyor | Belt condition and splice inspection | Inspection | Cover wear, edge damage, splice failure | 4 | Weeks | Stopped | Cover thickness above the limit; no edge damage beyond the trim limit; splices sound
Conveyor | Test belt rip, drift and pull cord protection | Failure finding | Protective device fails to operate | 6 | Months | Stopped | Each device trips the drive and raises the alarm in the control system
Air compressor | Replace intake filter, check separator differential pressure | Fixed interval | Filter blockage, separator saturation | 2000 | Hours | Stopped | Differential pressure below the limit after change; no oil carryover
Switchboard | Thermographic survey of connections and breakers under load | Condition monitoring | Loose or corroded connections | 12 | Months | Running | No hot spot more than the allowed rise above adjacent phases
Relief valve | Bench test lift pressure and reseat | Failure finding | Valve fails to lift at set pressure | 24 | Months | Stopped | Lifts within the tolerance of set pressure and reseats
Transformer | Oil sample for dissolved gas analysis, moisture and acidity | Condition monitoring | Insulation ageing, incipient faults | 12 | Months | Running | Gas ratios and trends inside the IEC 60599 limits; moisture and acidity within the oil specification
Transformer | Insulation resistance and polarisation index | Condition monitoring | Winding insulation degradation | 36 | Months | Stopped | Polarisation index above 1.5 and insulation resistance above the minimum for the voltage class
Switchboard | De-energised clean, inspect and torque check of connections | Fixed interval | Loose or corroded connections, contaminated insulation | 36 | Months | Stopped | All connections to the torque chart; no tracking or discolouration; insulation clean and dry
Switchboard | Circuit breaker operate and timing test | Failure finding | Mechanism stiff or slow, fails to trip | 36 | Months | Stopped | Trip and close times within the maker's limits on all poles
Protection relay | Secondary injection test against the protection settings | Failure finding | Relay fails to operate, settings drifted | 36 | Months | Stopped | Operates at the set values within tolerance; settings match the protection study
Variable speed drive | Cooling filter and fan check, capacitor condition, parameter backup | Inspection | Overheating, capacitor ageing, lost configuration | 6 | Months | Running | Filters clean, fans running, DC bus ripple within limit, parameters backed up and dated
Motor | Insulation resistance and polarisation index | Condition monitoring | Winding insulation breakdown | 12 | Months | Stopped | Polarisation index above 2 and insulation resistance above the minimum for the voltage class, temperature corrected
UPS | Battery capacity discharge test | Failure finding | Battery fails to carry the load | 12 | Months | Running | Holds the design load for the design autonomy; replace strings below 80 per cent capacity
Standby generator | Start and load test on load bank | Failure finding | Fails to start or to take load | 3 | Months | Running | Starts within the design time, takes rated load, no alarms, fuel and coolant within limits
Examples only. The intervals are typical starting points and every site sets its own from wear rates, failure history and the P-F interval. Copy a row to the Checklist tab and give it the tag and equipment it belongs to.

## Kinds of task
Kind of task | Suits | Example | Interval comes from
Fixed interval service or replacement | Wear or ageing that follows hours, tonnes or cycles closely enough to predict | Replace screen media at 1,200 operating hours | Measured wear rate or failure history, set short of the expected life
Inspection | Slow, visible degradation on items that cannot be instrumented cheaply | Walk the conveyor route, check idlers, skirts, cleaners and structure | How fast the defect grows, with margin to plan the repair
Condition monitoring (on-condition) | Failures that give measurable warning: vibration, temperature, oil, current | Vibration readings on the mill motor bearings every four weeks | The P-F interval, so at least two readings fall inside it
Failure finding | Hidden failures of protection: trips, interlocks, standby equipment, relief valves | Test the crusher low lube pressure trip every six months | The unavailability that can be tolerated for the protection, and the failure rate of the device

## Review
Signal | What it usually means | Action
No finding in years of doing the task | The interval is too short, the failure mode does not occur, or the task cannot see it | Extend the interval or remove the task, after checking failure history
Failures between tasks | The interval is too long, or the task does not address the failure mode that is occurring | Shorten the interval or change the kind of task, from the failure data
Task is done, failure happens anyway | The task is the wrong kind: an inspection cannot see a random failure | Replace with a condition task if the failure gives warning, or accept run to failure
Task has no failure mode written against it | It came from a vendor manual or a template, not from analysis | Trace it to a failure mode or remove it
Checklist comes back all ticks, no readings | The pass criteria are not measurable, so the task cannot be reviewed | Rewrite the criteria as readings and limits
PM compliance high, corrective backlog growing | The program is not addressing the dominant failures | Run the review on the worst actors first
Review task by task, starting with the equipment that costs the most. Record every change with its basis on the maintenance plan, so a change the history later proves wrong can be reversed.